## Sheet1
Electrical Service Demand Calculation
Convert Sq Meters to Sq Feet (1=YES, 0=NO) | 1
Building Area | 256660 |  | INPUT
Voltage | 480 |  | OUTPUT
Phase | 3
Wire | 4
kVA/SF
Lighting Load |  | 1.2 | 3315.1983 | kVA
Receptacles, Appliance and general purpose load |  | 1.5 | 4143.9979 | kVA
Technology (computers, printers, telephone, servers, etc..) |  | 1.5 | 4143.9979 | kVA
Plumbing and Fire Protection |  | 1 | 2762.6652 | kVA
HVAC |  | 10 | 27626.6525 | kVA
General Ventilation |  | 2 | 5525.3305 | kVA
Equipment (Pumps, etc..) |  | 1 | 2762.6652 | kVA
Misc. Other Loads (Elevator, Medical Eq, Etc..) |  |  | 300 | kVA
Subtotal Connected Load |  |  | 50580.5075 | kVA
Future Expansion | 20% | of Connected Load | 10116.1015 | kVA
Total Connected Load |  |  | 60696.609 | kVA
~Estimated Demand Load | 80% | of Total Connected Load | 48557.2872 | kVA
~ Demand Amps @ | 480 |  | 58405.3392 | Amps