## Sheet1
Electrical Service Demand Calculation
Building Area | 125000 | SF | INPUT
Voltage | 480 |  | OUTPUT
Phase | 3
Wire | 4
kVA/SF
Lighting Load |  | 1.2 | 150 | kVA
Receptacles, Appliance and general purpose load |  | 1.5 | 187.5 | kVA
Technology (computers, printers, telephone, servers, etc..) |  | 1.5 | 187.5 | kVA
Plumbing and Fire Protection |  | 1 | 125 | kVA
HVAC |  | 10 | 1250 | kVA
General Ventilation |  | 2 | 250 | kVA
Equipment (Pumps, etc..) |  | 1 | 125 | kVA
Misc. Other Loads (Elevator, Medical Eq, Etc..) |  |  | 300 | kVA
Subtotal Connected Load |  |  | 2575 | kVA
Future Expansion | 20% | of Connected Load | 515 | kVA
Total Connected Load |  |  | 3090 | kVA
~Estimated Demand Load | 80% | of Total Connected Load | 2472 | kVA
~ Demand Amps @ | 480 |  | 2973.3539 | Amps